## Inputs
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Inputs
Constants and Conversions
Parameter | Value | Unit | Source
Existing building-level steam loss | 15% | % | Assumption to convert from steam usage to heating, cooling and process loads. Accounts for steam losses through leaky traps, pipes, etc.
Enthalpy | 970 | Btu/lb
Btu/kBtu | 1000 | Btu/kBtu | Constant
Gas efficiency | 80% | % | Assumption
Btu per W | 3.412 | Btu/W | Constant
Btu per therm | 100000 | Btu/therm | Constant
Absorption chiller efficiency | 0.4 | COP | Assumption based on average chiller age and discussion with Mike Stone
Existing electric chiller efficiency | 1.25 | kW/ton | Assumption based on average chiller age and discussion with Mike Stone
New electric chiller efficiency | 0.5 | kW/ton | Assumption based on average chiller age and discussion with Mike Stone
Building heating system efficiency | 95% | % | Assumption to convert from steam usage to heating load
Btuh per ton | 12000 | Btuh/ton | Constant
New Energy Use
Building Type | Energy Use Intensity
| Electricity (kWh/sqft/y) | Thermal (therms/sqft/y) | Electricity (kBtu/sqft/y) | Steam (lbs/sqft/y) | Source
Admin | 4.5 | 0.08 | 15.354 | 9.4845 | Academic/adminstrative non-complex space
Athletic | 4.5 | 0.08 | 15.354 | 9.4845 | Academic/adminstrative non-complex space
Auditorium | 4.5 | 0.08 | 15.354 | 9.4845 | Academic/adminstrative non-complex space
Bioscience | 14 | 0.73 | 47.768 | 86.5464 | Lab/complex space
Chemistry | 14 | 0.73 | 47.768 | 86.5464 | Lab/complex space
Classroom | 4.5 | 0.08 | 15.354 | 9.4845 | Academic/adminstrative non-complex space
Data Center | 14 | 0.08 | 47.768 | 9.4845 | Lab/complex space
Engineering | 14 | 0.73 | 47.768 | 86.5464 | Lab/complex space
Library | 4.5 | 0.08 | 15.354 | 9.4845 | Academic/adminstrative non-complex space
Mixed Use | 7.6667 | 0.29667 | 26.1587 | 35.1718 | Average of engineering, classroom, and admin
Physics | 14 | 0.73 | 47.768 | 86.5464 | Lab/complex space
Residence | 3.1 | 0.12 | 10.5772 | 14.2268 | Housing non-complex space
Energy Splits
Building Type | Electricity |  |  |  | Steam
| Cooling & Heat Rejection | Vent & Fans | Interior and Exterior Lighting | Plugs and Misc. | Space Heating | DHW | Absorption | Process
Admin | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
Athletic | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
Auditorium | 26% | 31% | 27% | 16% | 90% | 10% | 0% | 0%
Bioscience | 25% | 35% | 18% | 22% | 70% | 30% | 0% | 0%
Chemistry | 25% | 35% | 18% | 22% | 70% | 30% | 0% | 0%
Classroom | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
Data Center | 5% | 4% | 1% | 90% | 80% | 20% | 0% | 0%
Engineering | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
Library | 16.6% | 19.26% | 24.58% | 39.56% | 80% | 20% | 0% | 0%
Mixed Use | 16% | 16.33% | 24.67% | 43% | 76.67% | 23.33% | 0% | 0%
Physics | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
Residence | 0% | 10% | 40% | 50% | 60% | 40% | 0% | 0%
New Peak Load
Peak Heating (therms/hr/1000sqft) |  | Peak Heating (Btuh/sqft) |  |  |  | Peak Cooling (tons/1000 sqft) | Peak Electricity (w/sqft) | Source
| Heating and DHW | Heating and DHW | Absorption | Process | Total Heating | Cooling | Non-cooling, non-heating
Admin | 0.1 | 10 | 0 | 0 | 10.1 | 1 | 1.39 | Academic/adminstrative non-complex space
Athletic | 0.1 | 10 | 0 | 0 | 10.1 | 1 | 1.39 | Academic/adminstrative non-complex space
Auditorium | 0.1 | 10 | 0 | 0 | 10.1 | 1 | 1.39 | Academic/adminstrative non-complex space
Bioscience | 0.34 | 34 | 0 | 7.1 | 41.44 | 2.5 | 3.4 | Lab/complex space
Chemistry | 0.34 | 34 | 0 | 1.6 | 35.94 | 2.5 | 3.4 | Lab/complex space
Classroom | 0.1 | 10 | 0 | 0 | 10.1 | 1 | 1.39 | Academic/adminstrative non-complex space
Data Center | 0.1 | 10 | 0 | 0 | 10.1 | 2.5 | 3.4 | Lab/complex space
Engineering | 0.34 | 34 | 0 | 1.6 | 35.94 | 2.5 | 3.4 | Lab/complex space
Library | 0.1 | 10 | 0 | 0 | 10.1 | 1 | 1.39 | Academic/adminstrative non-complex space
Mixed Use | 0.18 | 18 | 0 | 0.53333 | 18.7133 | 1.5 | 2.06 | Average of engineering, classroom, and admin
Physics | 0.34 | 34 | 0 | 1.6 | 35.94 | 2.5 | 3.4 | Lab/complex space
Residence | 0.14 | 14 | 0 | 0 | 14.14 | 0.7 | 0.98 | Housing non-complex space
Steam Load Splits
| Space Heating | DHW | Absorption | Process
Admin | 90% | 10% | 0% | 0%
Athletic | 60% | 40% | 0% | 0%
Auditorium | 90% | 10% | 0% | 0%
Bioscience | 80% | 20% | 0% | 0%
Chemistry | 90% | 10% | 0% | 0%
Classroom | 90% | 10% | 0% | 0%
Data Center | 60% | 40% | 0% | 0%
Engineering | 80% | 20% | 0% | 0%
Library | 90% | 10% | 0% | 0%
Mixed Use | 86.67% | 13.33% | 0% | 0%
Physics | 80% | 20% | 0% | 0%
Residence | 50% | 50% | 0% | 0%
Peak Load Diversity
| Heating | Cooling | Source
Campus | 80% | 90% | Assumption from 2015 study
Node | 85% | 95% | Assumption from 2015 study
Clusters
Clusters | Year Transferred
Biosciences North | 2025
Biosciences South | 2030
Business | 2035
Edwards | 2040
Engineering Birge | 2040
Engineering Bowles | 2045
Engineering Cory | 2035
Engineering Evans | 2030
Engineering Lewis | 2040
Engineering North Halls | 2035
Law Central | 2040
Law East | 2035
Law West | 2040
Libraries Moses | 2045
Libraries Moffitt | 2030
Libraries Dwinelle | 2045
Life Sciences | 2045
Lower Offices East | 2045
None | 2500
Oxford Tract | 2025
Peoples Park | 2045
University | 2030
Cooling Efficiencies
Building Area (sqft) |  | Cooling Type | Cooling Efficiency
Lower bound | Upper bound |  | Unit | Value | Unit | Value
0 | 10000 | Packaged Single Zone, DX | EER | 10 | kW/ton | 1.2
10000 | 150000 | Packaged VAV, DX | EER | 9.7 | kW/ton | 1.2371
150000 | 10000000 | Water-cooled chiller | kW/ton | 0.585 | kW/ton | 0.585
Note on G28: Erica Levine: UC whole-building energy performance targets 2025+ compliance target
Note on B38: Erica Levine: Average of engineering, classroom, and admin
Note on B55: Erica Levine: Average of engineering, classroom, and admin
Note on J61: Erica Levine: UC whole-building energy performance targets 2015-2016 compliance target
Note on F62: Erica Levine: Average peak condensate from previous study
Note on B72: Erica Levine: Average of engineering, classrom, and admin
Note on B87: Erica Levine: Average of engineering, classrom, and admin
Note on B124: Erica Levine: From Title 24

## Annual Energy Calc
Client | UC Berkeley | [6 empty] | Input
Project | Campus energy study update | [6 empty] | Lookup
Job Number | 267147 | [6 empty] | Calculation
Output
Check
Annual Energy Calculation
Metadata | [7 empty] | Annual Energy Use | [11 empty] | Check
CAAN | Building Name | Building Type | Year Constructed | Year Demolished | Building Area (sqft) | Node | Cluster | Electricity Use (kWh/y) | Electricity Split (%) |  |  |  |  | Steam Use (kBtu/y) | Steam Split (%) |  |  |  |  | Electricity Use (kWh/y) | Electricity Split (%) |  |  |  | Steam Split (%) |  |  |  | Electricity Split (%) |  |  |  | Steam Split (%)
[9 empty] | Cooling & Heat Rejection | Vent & Fans | Interior and Exterior Lighting | Plugs and Misc. | Check |  | Space Heating | DHW | Absorption | Process | Check |  | Cooling & Heat Rejection | Vent & Fans | Interior and Exterior Lighting | Plugs and Misc. | Space Heating | DHW | Absorption | Process | Cooling & Heat Rejection | Vent & Fans | Interior and Exterior Lighting | Plugs and Misc. | Space Heating | DHW | Absorption | Process
1215 | Alumni House | Admin | 1954 |  | 15326 | Lower Sproul offices | Lower Offices East | 143076 | 10% | 12% | 22% | 56% |  | 463628.9833 | 80% | 20% | 0% | 0% |  | 143076 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1298 | Bancroft Library (Doe Annex) | Library | 1949 |  | 132394 | Engineering, Physics and Chemistry | Libraries Moffitt | 1703847.9321 | 16.6% | 19.26% | 24.58% | 39.56% |  | 6962491.1059 | 80% | 20% | 0% | 0% |  | 1703847.9321 | 16.6% | 19.26% | 24.58% | 39.56% | 80% | 20% | 0% | 0%
1793 | Barker Hall | Bioscience | 1964 |  | 86091 | Biosciences | Biosciences North | 2816021 | 25% | 35% | 18% | 22% |  | 31229749.5634 | 56% | 24% | 0% | 20% |  | 2816021 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1761 | Barrows Hall | Classroom | 1964 |  | 193202 | Business and Law | Law West | 1260397 | 26% | 23% | 26% | 25% |  | 4967094.9765 | 80% | 20% | 0% | 0% |  | 1260397 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1788 | Bechtel Engineering Center | Classroom | 1980 |  | 47954 | Engineering, Physics and Chemistry | Engineering Cory | 405277 | 26% | 23% | 26% | 25% |  | 1450663.2042 | 80% | 20% | 0% | 0% |  | 405277 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1220 | Birge Hall | Physics | 1964 |  | 94175 | Engineering, Physics and Chemistry | Engineering Birge | 2985683 | 12% | 14% | 26% | 48% |  | 7154934.2645 | 70% | 30% | 0% | 0% |  | 2985683 | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
1322 | Blum Hall | Mixed Use | 1914 |  | 23815 | Engineering, Physics and Chemistry | Engineering Cory | 113879 | 16% | 16.33% | 24.67% | 43% |  | 1669338.3798 | 76.67% | 23.33% | 0% | 0% |  | 113879 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1231 | Boalt Hall | Classroom | 1966 |  | 277521 | Business and Law | Law East | 1833318.2365 | 26% | 23% | 26% | 25% |  | 7134880.41 | 80% | 20% | 0% | 0% |  | 1833318.2365 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1230 | Bowles Hall | Residence | 1929 |  | 73700 | Engineering, Physics and Chemistry | Engineering Bowles | 141083 | 0% | 10% | 40% | 50% |  | 750202.5647 | 60% | 40% | 0% | 0% |  | 141083 | 0% | 10% | 40% | 50% | 60% | 40% | 0% | 0%
1270 | California Hall | Admin | 1905 |  | 56343 | Engineering, Physics and Chemistry | Libraries Dwinelle | 388057 | 10% | 12% | 22% | 56% |  | 1704440.024 | 80% | 20% | 0% | 0% |  | 388057 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1271 | California Memorial Stadium | Athletic | 1923 |  | 261091 | Business and Law | Law East | 2692449 | 24% | 26% | 29% | 21% |  | 1876212.8 | 60% | 40% | 0% | 0% |  | 2692449 | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
1799 | Calvin Laboratory | Bioscience | 1963 |  | 33167 | Business and Law | Law East | 370341 | 25% | 35% | 18% | 22% |  | 4199764.7067 | 56% | 24% | 0% | 20% |  | 370341 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1374 | Central Heating Plant | Mechanical | 1930 |  | 20385 | N/A | None | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0% | 0% | 0% | 0% | FLAG |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
1784 | Cesar E. Chavez Student Center | Admin | 1960 |  | 104016 | Lower Sproul offices | Lower Offices East | 1010700 | 10% | 12% | 22% | 56% |  | 3146602.6577 | 80% | 20% | 0% | 0% |  | 1010700 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1233 | Cheit Hall | Classroom | 1995 |  | 32120 | Business and Law | Business | 604834.7585 | 26% | 23% | 26% | 25% |  | 825783.8462 | 80% | 20% | 0% | 0% |  | 604834.7585 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1325 | Cory Hall | Engineering | 1950 | 2025 | 206054 | Engineering, Physics and Chemistry | Engineering Cory | 4902265 | 12% | 14% | 26% | 48% |  | 12063124.2706 | 70% | 30% | 0% | 0% |  | 4902265 | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
1297 | David Gardner Stacks | Library | 1994 |  | 189425 | Engineering, Physics and Chemistry | Libraries Moffitt | 1509589 | 16.6% | 19.26% | 24.58% | 39.56% |  | 4447741 | 80% | 20% | 0% | 0% |  | 1509589 | 16.6% | 19.26% | 24.58% | 39.56% | 80% | 20% | 0% | 0%
1323 | Davis Hall | Engineering | 1967 | 2023 | 137806 | Engineering, Physics and Chemistry | Engineering Cory | 1165656 | 12% | 14% | 26% | 48% |  | 4653845.4588 | 70% | 30% | 0% | 0% |  | 1165656 | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
1301 | Doe Memorial Library | Library | 1917 |  | 166514 | Engineering, Physics and Chemistry | Libraries Moffitt | 958948 | 16.6% | 19.26% | 24.58% | 39.56% |  | 6733071.2706 | 80% | 20% | 0% | 0% |  | 958948 | 16.6% | 19.26% | 24.58% | 39.56% | 80% | 20% | 0% | 0%
1419 | Donner Laboratory | Chemistry | 1942 | 2030 | 53234 | Engineering, Physics and Chemistry | Engineering Cory | 1056122 | 25% | 35% | 18% | 22% |  | 8669654.5882 | 56% | 24% | 0% | 20% |  | 1056122 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1227 | Durant Hall | Admin | 1911 |  | 21866 | Engineering, Physics and Chemistry | Libraries Dwinelle | 188788 | 10% | 12% | 22% | 56% |  | 0 | 80% | 20% | 0% | 0% |  | 188788 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1295 | Dwinelle Hall | Classroom | 1952 |  | 305268 | Engineering, Physics and Chemistry | Libraries Dwinelle | 1175091 | 26% | 23% | 26% | 25% |  | 7848237.3333 | 80% | 20% | 0% | 0% |  | 1175091 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1095 | Earl Warren Hall | Data Center | 2003 |  | 69032 | Biosciences | Biosciences North | 9034448 | 5% | 4% | 1% | 90% |  | 1559747.4471 | 80% | 20% | 0% | 0% |  | 9034448 | 5% | 4% | 1% | 90% | 80% | 20% | 0% | 0%
1318 | Edwards Stadium / Goldman Field | Athletic | 1932 | 2040 | 59326 | Lower Sproul offices | Edwards | 47770 | 24% | 26% | 29% | 21% |  | 0 | 60% | 40% | 0% | 0% |  | 47770 | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
1783 | Etcheverry Hall | Engineering | 1964 |  | 177281 | Engineering, Physics and Chemistry | Engineering North Halls | 3609041 | 12% | 14% | 26% | 48% |  | 10378651.8768 | 70% | 30% | 0% | 0% |  | 3609041 | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
1790 | Evans Hall | Mixed Use | 1971 | 2025 | 270413 | Engineering, Physics and Chemistry | Engineering Evans | 2202163 | 16% | 16.33% | 24.67% | 43% |  | 14907615.0353 | 76.67% | 23.33% | 0% | 0% |  | 2202163 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1340 | Faculty Club | Admin | 1903 |  | 35483 | Business and Law | Business | 337170 | 10% | 12% | 22% | 56% |  | 3167709.8199 | 60% | 40% | 0% | 0% |  | 337170 | 10% | 12% | 22% | 56% | 60% | 40% | 0% | 0%
1789 | Genetics & Plant Biology | Bioscience | 1990 |  | 26321 | Biosciences | Biosciences South | 495636.8518 | 25% | 35% | 18% | 22% |  | 0 | 56% | 24% | 0% | 20% |  | 495636.8518 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1236 | Gerson Bakar Faculty Building | Admin | 1995 |  | 106295 | Business and Law | Business | 0 | 10% | 12% | 22% | 56% |  | 0 | 80% | 20% | 0% | 0% |  |  | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1355 | Giannini Hall | Classroom | 1930 |  | 68701 | Biosciences | Biosciences South | 454653 | 26% | 23% | 26% | 25% |  | 5595752.077 | 80% | 20% | 0% | 0% |  | 454653 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1410 | Giauque Laboratory | Chemistry | 1954 |  | 25996 | Engineering, Physics and Chemistry | Engineering Lewis | 868207 | 25% | 35% | 18% | 22% |  | 1975042.9641 | 70% | 30% | 0% | 0% |  | 868207 | 25% | 35% | 18% | 22% | 70% | 30% | 0% | 0%
1356 | Gilman Hall | Chemistry | 1917 |  | 44182 | Engineering, Physics and Chemistry | Engineering Lewis | 682572 | 25% | 35% | 18% | 22% |  | 3356722.1202 | 70% | 30% | 0% | 0% |  | 682572 | 25% | 35% | 18% | 22% | 70% | 30% | 0% | 0%
1424 | Hargrove Music Library | Library | 2004 |  | 29063 | Business and Law | Law West | 341660 | 16.6% | 19.26% | 24.58% | 39.56% |  | 827514.9882 | 80% | 20% | 0% | 0% |  | 341660 | 16.6% | 19.26% | 24.58% | 39.56% | 80% | 20% | 0% | 0%
1371 | Haviland Hall | Mixed Use | 1924 |  | 51020 | Engineering, Physics and Chemistry | Engineering Evans | 229315 | 16% | 16.33% | 24.67% | 43% |  | 4294276.8442 | 76.67% | 23.33% | 0% | 0% |  | 229315 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1267 | Hazardous Materials Facility | Mechanical | 1999 |  | 23432 | N/A | None | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0% | 0% | 0% | 0% | FLAG |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
1097 | Hearst Field Annex | Mixed Use | 1999 |  | 34825 | Business and Law | Law West | 81065 | 16% | 16.33% | 24.67% | 43% |  | 0 | 76.67% | 23.33% | 0% | 0% |  | 81065 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1372 | Hearst Memorial Gymnasium | Athletic | 1927 |  | 124197 | Business and Law | Law West | 602605 | 24% | 26% | 29% | 21% |  | 20178686.6555 | 51% | 34% | 0% | 15% |  | 602605 | 24% | 26% | 29% | 21% | 51% | 34% | 0% | 15%
1373 | Hearst Memorial Mining Building | Classroom | 1907 |  | 141461 | Engineering, Physics and Chemistry | Engineering Cory | 4202949 | 26% | 23% | 26% | 25% |  | 8281623.3727 | 80% | 20% | 0% | 0% |  | 4202949 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1423 | Hertz Memorial Concert Hall | Classroom | 1958 |  | 30160 | Business and Law | Law Central | 327029 | 26% | 23% | 26% | 25% |  | 1710966.8254 | 80% | 20% | 0% | 0% |  | 327029 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1375 | Hesse Hall | Engineering | 1924 | 2025 | 41363 | Engineering, Physics and Chemistry | Engineering Evans | 426155 | 12% | 14% | 26% | 48% |  | 2899384.5646 | 70% | 30% | 0% | 0% |  | 426155 | 12% | 14% | 26% | 48% | 70% | 30% | 0% | 0%
1809 | Hildebrand Hall | Chemistry | 1966 |  | 128126 | Engineering, Physics and Chemistry | Engineering Lewis | 4509238 | 1% | 46.2% | 23.76% | 29.04% |  | 40432176.2059 | 38.5% | 16.5% | 25% | 20% |  | 4509238 | 1% | 46.2% | 23.76% | 29.04% | 38.5% | 16.5% | 25% | 20%
1376 | Hilgard Hall | Bioscience | 1917 |  | 77055 | Biosciences | Biosciences South | 750964 | 25% | 35% | 18% | 22% |  | 10460320.2353 | 56% | 24% | 0% | 20% |  | 750964 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1390 | International House | Residence | 1930 |  | 185200 | Business and Law | Law East | 1432521 | 0% | 10% | 40% | 50% |  | 16533547.2941 | 60% | 40% | 0% | 0% |  | 1432521 | 0% | 10% | 40% | 50% | 60% | 40% | 0% | 0%
1032 | Jacobs | Engineering | 2015 |  | 24000 | Engineering, Physics and Chemistry | Engineering North Halls | 1146432 | 12% | 14% | 26% | 48% |  | 2077113.4021 | 70% | 30% | 0% | 0%
1796 | Koshland Hall | Bioscience | 1990 |  | 153700 | Biosciences | Biosciences North | 7630965 | 25% | 35% | 18% | 22% |  | 48872025.4314 | 56% | 24% | 0% | 20% |  | 7630965 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1486 | Kroeber Hall | Classroom | 1959 |  | 117814 | Business and Law | Law Central | 682886 | 26% | 23% | 26% | 25% |  | 4351656.2235 | 80% | 20% | 0% | 0% |  | 682886 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1782 | Latimer Hall | Chemistry | 1963 |  | 182943 | Engineering, Physics and Chemistry | Engineering Lewis | 5647091.8418 | 1% | 46.2% | 23.76% | 29.04% |  | 58744170 | 38.5% | 16.5% | 25% | 20% |  | 5647091.8418 | 1% | 46.2% | 23.76% | 29.04% | 38.5% | 16.5% | 25% | 20%
1405 | LeConte Hall | Mixed Use | 1924 |  | 148032 | Engineering, Physics and Chemistry | Engineering Birge | 1291089 | 16% | 16.33% | 24.67% | 43% |  | 11246713.3426 | 76.67% | 23.33% | 0% | 0% |  | 1291089 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1292 | Lewis Hall | Chemistry | 1948 | 2028 | 68146 | Engineering, Physics and Chemistry | Engineering Lewis | 1568177 | 25% | 35% | 18% | 22% |  | 8628973.549 | 56% | 24% | 0% | 20% |  | 1568177 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1444 | Li Ka Shing Center | Bioscience | 2011 |  | 220703 | Biosciences | Biosciences South | 10551319 | 25% | 35% | 18% | 22% |  | 163657759.3535 | 56% | 24% | 0% | 20% |  | 10551319 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1225 | Life Sciences Addition | Bioscience | 1988 |  | 201824 | Engineering, Physics and Chemistry | Life Sciences | 7404877 | 25% | 35% | 18% | 22% |  | 149658426.1373 | 56% | 24% | 0% | 20% |  | 7404877 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1762 | McCone Hall | Mixed Use | 1961 |  | 123612 | Engineering, Physics and Chemistry | Engineering Evans | 1697015 | 16% | 16.33% | 24.67% | 43% |  | 8664717.8588 | 76.67% | 23.33% | 0% | 0% |  | 1697015 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1321 | McLaughlin Hall | Admin | 1931 |  | 49388 | Engineering, Physics and Chemistry | Engineering Evans | 262494 | 10% | 12% | 22% | 56% |  | 3461905.6856 | 80% | 20% | 0% | 0% |  | 262494 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1302F | Minor Hall | Mixed Use | 1941 |  | 46204 | Business and Law | Business | 58723 | 16% | 16.33% | 24.67% | 43% |  | 48477142.2353 | 61.33% | 18.67% | 0% | 20% |  | 58723 | 39.5% | 13.03% | 15.13% | 32.35% | 56% | 24% | 0% | 20% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1302 | Minor Hall Addition | Mixed Use | 1978 |  | 55516 | Business and Law | Business | 1249244 | 16% | 16.33% | 24.67% | 43% |  | 4217821.403 | 76.67% | 23.33% | 0% | 0% |  | 1249244 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1791 | MLK, Jr. Student Union | Admin | 1961 |  | 102901 | Lower Sproul offices | Lower Offices East | 264751 | 10% | 12% | 22% | 56% |  | 3112872.6357 | 80% | 20% | 0% | 0% |  | 264751 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1299 | Moffitt Undergraduate Library | Library | 1970 |  | 130581 | Engineering, Physics and Chemistry | Libraries Moffitt | 1518099 | 1% | 22.86% | 29.18% | 46.96% |  | 6867146.9334 | 48% | 12% | 40% | 0% |  | 1518099 | 1% | 22.86% | 29.18% | 46.96% | 48% | 12% | 40% | 0%
1382 | Morgan Hall | Mixed Use | 1953 |  | 56637 | Biosciences | Biosciences South | 975303 | 16% | 16.33% | 24.67% | 43% |  | 7945085.5098 | 61.33% | 18.67% | 0% | 20% |  | 975303 | 39.5% | 13.03% | 15.13% | 32.35% | 56% | 24% | 0% | 20% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1422 | Morrison Hall | Classroom | 1958 |  | 40706 | Business and Law | Law Central | 180419 | 26% | 23% | 26% | 25% |  | 2309237.9176 | 80% | 20% | 0% | 0% |  | 180419 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1324 | Moses Hall | Classroom | 1931 |  | 40835 | Engineering, Physics and Chemistry | Libraries Moses | 1699 | 26% | 23% | 26% | 25% |  | 1235305.3331 | 80% | 20% | 0% | 0% |  | 1699 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1346 | Mulford Hall | Classroom | 1948 |  | 93420 | Biosciences | Biosciences South | 500760 | 26% | 23% | 26% | 25% |  | 13105035.3713 | 64% | 16% | 0% | 20% |  | 500760 | 26% | 23% | 26% | 25% | 64% | 16% | 0% | 20%
1206 | North Gate Hall | Classroom | 1906 |  | 23533 | Engineering, Physics and Chemistry | Engineering Cory | 0 | 26% | 23% | 26% | 25% |  | 1916781.9046 | 80% | 20% | 0% | 0% |  |  | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1229 | Northwest Animal Facility | Bioscience | 1991 |  | 52845 | Biosciences | Biosciences North | 1281704 | 25% | 35% | 18% | 22% |  | 19169670.6471 | 56% | 24% | 0% | 20% |  | 1281704 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1377 | O'Brien Hall | Classroom | 1959 | 2025 | 41297 | Engineering, Physics and Chemistry | Engineering Evans | 494276 | 26% | 23% | 26% | 25% |  | 2894758.2226 | 80% | 20% | 0% | 0% |  | 494276 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1801 | Pimentel Hall | Classroom | 1964 |  | 14524 | Engineering, Physics and Chemistry | Engineering Lewis | 83616 | 26% | 23% | 26% | 25% |  | 0 | 80% | 20% | 0% | 0% |  | 83616 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1365 | Recreational Sports Facility | Athletic | 1984 |  | 187982 | Lower Sproul offices | Edwards | 889276 | 24% | 26% | 29% | 21% |  | 4501725.4941 | 60% | 40% | 0% | 0% |  | 889276 | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
1391 | Simon Hall | Classroom | 1966 |  | 36180 | Business and Law | Law East | 239006.9717 | 26% | 23% | 26% | 25% |  | 1362496.2353 | 80% | 20% | 0% | 0% |  | 239006.9717 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1277 | Simpson Student-Athlete High Performance Center | Athletic | 2011 |  | 139682 | Business and Law | Law East | 2246028 | 24% | 26% | 29% | 21% |  | 2606521.2353 | 60% | 40% | 0% | 0% |  | 2246028 | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
1237 | Soda Hall | Mixed Use | 1994 |  | 109588 | Engineering, Physics and Chemistry | Engineering North Halls | 3719212 | 16% | 16.33% | 24.67% | 43% |  | 6415666.1 | 76.67% | 23.33% | 0% | 0% |  | 3719212 | 39.5% | 13.03% | 15.13% | 32.35% | 70% | 30% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1484 | South Hall | Classroom | 1873 |  | 30401 | Engineering, Physics and Chemistry | Libraries Dwinelle | 117472 | 26% | 23% | 26% | 25% |  | 919664.9304 | 80% | 20% | 0% | 0% |  | 117472 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1210 | Sproul Hall | Admin | 1941 |  | 110919 | Business and Law | Law West | 910249 | 10% | 12% | 22% | 56% |  | 3355426.2824 | 80% | 20% | 0% | 0% |  | 910249 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1149 | Stanley Hall | Chemistry | 2006 |  | 304333 | Engineering, Physics and Chemistry | Engineering Evans | 14130264.1519 | 13% | 40.6% | 20.88% | 25.52% |  | 53831137.1176 | 45.5% | 19.5% | 25% | 10% |  | 14130264.1519 | 13% | 40.6% | 20.88% | 25.52% | 45.5% | 19.5% | 25% | 10%
1150 | Starr East Asian Library | Library | 2007 |  | 65860 | Engineering, Physics and Chemistry | Engineering Evans | 862821 | 1% | 22.86% | 29.18% | 46.96% |  | 2584220.3647 | 48% | 12% | 40% | 0% |  | 862821 | 1% | 22.86% | 29.18% | 46.96% | 48% | 12% | 40% | 0%
1661 | Steam Tunnel | mechanical | 1930 |  | 13720 | N/A | None | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0% | 0% | 0% | 0% | FLAG |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
1488 | Stephens Hall | Classroom | 1923 |  | 58733 | Engineering, Physics and Chemistry | Libraries Moses | 376339 | 26% | 23% | 26% | 25% |  | 1776740.2505 | 80% | 20% | 0% | 0% |  | 376339 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1495 | Stern Hall | Residence | 1942 |  | 86959 | Engineering, Physics and Chemistry | Engineering Bowles | 265813 | 0% | 10% | 40% | 50% |  | 11102202.3294 | 60% | 40% | 0% | 0% |  | 265813 | 0% | 10% | 40% | 50% | 60% | 40% | 0% | 0%
1152 | Sutardja Dai Hall | Engineering | 2009 |  | 154706 | Engineering, Physics and Chemistry | Engineering Cory | 7733627 | 1% | 15.75% | 29.25% | 54% |  | 9057032.1537 | 42% | 18% | 40% | 0% |  | 7733627 | 1% | 15.75% | 29.25% | 54% | 42% | 18% | 40% | 0%
1808 | Tan Hall | Chemistry | 1996 |  | 116121 | Engineering, Physics and Chemistry | Engineering Lewis | 3804708 | 25% | 35% | 18% | 22% |  | 56486576.7843 | 56% | 24% | 0% | 20% |  | 3804708 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1594 | University Hall | Admin | 1959 |  | 150887 | Biosciences | University | 1372861 | 10% | 12% | 22% | 56% |  | 2973103.6353 | 80% | 20% | 0% | 0% |  | 1372861 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1439 | University House | residence | 1911 |  | 18112 | Biosciences | Biosciences North | 140096.2222 | 0% | 10% | 40% | 50% |  | 1616930.9319 | 60% | 40% | 0% | 0% |  | 140096.2222 | 0% | 10% | 40% | 50% | 60% | 40% | 0% | 0%
1406 | Valley Life Sciences Building | Bioscience | 1930 |  | 420885 | Engineering, Physics and Chemistry | Life Sciences | 8607761 | 25% | 35% | 18% | 22% |  | 70423221.0588 | 56% | 24% | 0% | 20% |  | 8607761 | 25% | 35% | 18% | 22% | 56% | 24% | 0% | 20%
1234 | Walter A. Haas Student Services Building | Admin | 1995 |  | 95712 | Business and Law | Business | 1802302.1297 | 10% | 12% | 22% | 56% |  | 2460691.8893 | 80% | 20% | 0% | 0% |  | 1802302.1297 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1360 | Walter A. Haas, Jr. Pavilion | Athletic | 1933 |  | 238065 | Lower Sproul offices | Edwards | 3774175 | 24% | 26% | 29% | 21% |  | 5701095.21 | 60% | 40% | 0% | 0% |  | 3774175 | 24% | 26% | 29% | 21% | 60% | 40% | 0% | 0%
1202 | Wellman Hall | Classroom | 1912 |  | 43910 | Biosciences | Biosciences South | 519010 | 26% | 23% | 26% | 25% |  | 5960841.7563 | 64% | 16% | 0% | 20% |  | 519010 | 26% | 23% | 26% | 25% | 64% | 16% | 0% | 20%
1552 | Wheeler Hall | Mixed Use | 1917 |  | 139436 | Engineering, Physics and Chemistry | Libraries Dwinelle | 633096 | 16% | 16.33% | 24.67% | 43% |  | 3584806.8609 | 76.67% | 23.33% | 0% | 0% |  | 633096 | 39.5% | 13.03% | 15.13% | 32.35% | 80% | 20% | 0% | 0% | FLAG | FLAG | FLAG | FLAG | FLAG | FLAG
1553 | Women's Faculty Club | Admin | 1923 |  | 18474 | Business and Law | Business | 98954 | 10% | 12% | 22% | 56% |  | 1649248.1248 | 80% | 20% | 0% | 0% |  | 98954 | 10% | 12% | 22% | 56% | 80% | 20% | 0% | 0%
1797 | Wurster Hall | Classroom | 1964 |  | 222434 | Business and Law | Law Central | 1750749 | 26% | 23% | 26% | 25% |  | 3615931.7647 | 80% | 20% | 0% | 0% |  | 1750749 | 26% | 23% | 26% | 25% | 80% | 20% | 0% | 0%
1802 | Zellerbach Hall | Auditorium | 1968 |  | 153118 | Lower Sproul offices | Lower Offices East | 910890 | 26% | 31% | 27% | 16% |  | 1663546.5765 | 90% | 10% | 0% | 0% |  | 910890 | 26% | 31% | 27% | 16% | 90% | 10% | 0% | 0%
New Buildings
1325 (N) | Cory Hall (N) | Engineering | 2028 |  | 200000 | Engineering, Physics and Chemistry | Engineering Cory | 9553600 | 12% | 14% | 26% | 48% |  | 16790000 | 70% | 30% | 0% | 0%
1323 (N) | Davis Hall (N) | Engineering | 2025 |  | 150000 | Engineering, Physics and Chemistry | Engineering Cory | 7165200 | 12% | 14% | 26% | 48% |  | 12592500 | 70% | 30% | 0% | 0%
1419 (N) | Donner Laboratory (N) | Chemistry | 2028 |  | 100000 | Engineering, Physics and Chemistry | Engineering Cory | 4776800 | 25% | 35% | 18% | 22% |  | 8395000 | 70% | 30% | 0% | 0%
1318 (N) | Edwards Stadium / Goldman Field New Quad (N) | Mixed Use | 2040 |  | 1500000 | Lower Sproul offices | Edwards | 39238000 | 16% | 16.33% | 24.67% | 43% |  | 51175000 | 69% | 21% | 0% | 10%
1790 (N) | Evans Hall (N) | Classroom | 2030 |  | 165000 | Engineering, Physics and Chemistry | Engineering Evans | 2533410 | 26% | 23% | 26% | 25% |  | 1518000 | 80% | 20% | 0% | 0%
1375 (N) | Hesse/O'Brien (N) | Engineering | 2023 |  | 225000 | Engineering, Physics and Chemistry | Engineering Evans | 10747800 | 12% | 14% | 26% | 48% |  | 18888750 | 70% | 30% | 0% | 0%
1292 (N) | Lewis Hall (N) | Chemistry | 2040 |  | 87500 | Engineering, Physics and Chemistry | Engineering Lewis | 4179700 | 25% | 35% | 18% | 22% |  | 7345625 | 70% | 30% | 0% | 0%
CAAN? | Lewis Hall Addition | Chemistry | 2028 |  | 90000 | Engineering, Physics and Chemistry | Engineering Lewis | 4299120 | 25% | 35% | 18% | 22% |  | 7555500 | 70% | 30% | 0% | 0%
1785 | Oxford Tract | Residence | 2025 |  | 1050000 | Biosciences | Oxford Tract | 11106060 | 0% | 10% | 40% | 50% |  | 14490000 | 48% | 32% | 0% | 20%
1601 | Peoples Park | Residence | 2023 |  | 432000 | Lower Sproul offices | Peoples Park | 4569350.4 | 0% | 10% | 40% | 50% |  | 5961600 | 60% | 40% | 0% | 0%
1774 (N) | Tolman Hall (N) (Climate Science Building) | Bioscience | 2025 |  | 292500 | Biosciences | Biosciences North | 13972140 | 25% | 35% | 18% | 22% |  | 24555375 | 56% | 24% | 0% | 20%
Note on F12: Erica Levine: Update with latest
Note on L12: Erica Levine: All hard-entered values per 2015 study
Note on R12: Erica Levine: All hard-entered values per 2015 study
Note on U16: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U25: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U33: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U41: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U50: Afaan Naqvi: 30% to 15% (7/14 process peak-to-energy match)
Note on U54: Afaan Naqvi: 40% to 25% (7/14 process peak-to-energy match)
Note on U55: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U58: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U60: Afaan Naqvi: 40% to 25% (7/14 process peak-to-energy match)
Note on U62: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U63: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U64: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U67: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U71: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U74: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U76: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on L85: Afaan Naqvi: See Stanley sub-meter data
Note on U85: Afaan Naqvi: 40% to 25% (7/14 process peak-to-energy match)
Note on U91: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U94: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U97: Afaan Naqvi: 40% to 20% (7/14 process peak-to-energy match)
Note on U107: Erica Levine: Typical for existing biosciences buildings
Note on U112: Erica Levine: Typical for existing biosciences buildings
Note on U114: Erica Levine: Typical for existing biosciences buildings

## Peak Load Calc
Client | UC Berkeley | [7 empty] | Input
Project | Campus energy study update | [7 empty] | Lookup
Job Number | 267147 | [7 empty] | Calculation
Output
Check
Annual Energy Calculation
Metadata | [8 empty] | Peak Load | [16 empty] | Check
CAAN | Building Name | Building Type | Year Constructed | Year Demolished | Building Area (sqft) | Node (4) | Cluster | Cooling Type | Peak Steam Intensity (Btuh/sqft) | Peak Steam Use (Btu/h) |  |  |  |  | Peak Steam Split (%) |  |  |  |  | Peak Heating (kBtu/h) | Peak Cooling (tons) |  |  | Building Chillers |  | Peak Steam Use (Btu/h) |  |  |  |  | Peak Steam Use Check |  |  |  |  | Steam Split Check |  |  |  | Steam Split (%)
[10 empty] | Total | Heating | DHW | Absorption | Process | Heating | DHW | Absorption | Process | Check | Peak Heating | Existing Chiller Capacity | Total Chiller Capacity | New Chiller Capacity | Efficiency (kW/ton) | Peak Power (kW) | Total | Heating | DHW | Absorption | Process | Total | Space Heating | DHW | Absorption | Process | Space Heating | DHW | Absorption | Process | Space Heating | DHW | Absorption | Process
1215 | Alumni House | Admin | 1954 |  | 15326 | Lower Sproul offices | Lower Offices East | Packaged VAV, DX | 17.1 | 262074.6 | 235867.14 | 26207.46 | 0 | 0 | 90% | 10% | 0% | 0% |  | 211.6252 | 0 | 15.326 | 15.326 | 1.2371 | 18.96 | 262074.6 | 235867.14 | 26207.46 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1298 | Bancroft Library (Doe Annex) | Library | 1949 |  | 132394 | Engineering, Physics and Chemistry | Libraries Moffitt | Packaged VAV, DX | 32 | 4236608 | 3812947.2 | 423660.8 | 0 | 0 | 90% | 10% | 0% | 0% |  | 3421.061 | 250 | 250 | 0 | 1.2371 | 0 | 4236608 | 3812947.2 | 423660.8 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1793 | Barker Hall | Bioscience | 1964 |  | 86091 | Biosciences | Biosciences North | Packaged VAV, DX | 32 | 2754912 | 1542750.72 | 385687.68 | 0 | 826473.6 | 56% | 14% | 0% | 30% |  | 1557.214 | 200 | 200 | 0 | 1.2371 | 0 | 2754912 | 1542750.72 | 385687.68 | 0 | 826473.6 | [5 empty] | 56% | 14% | 0% | 30%
1761 | Barrows Hall | Classroom | 1964 |  | 193202 | Business and Law | Law West | Water-cooled chiller | 11.3 | 2183182.6 | 1964864.34 | 218318.26 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1762.9199 | 0 | 193.202 | 193.202 | 0.585 | 113.0232 | 2183182.6 | 1964864.34 | 218318.26 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1788 | Bechtel Engineering Center | Classroom | 1980 |  | 47954 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 32 | 1534528 | 1381075.2 | 153452.8 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1239.1314 | 0 | 47.954 | 47.954 | 1.2371 | 59.3245 | 1534528 | 1381075.2 | 153452.8 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1220 | Birge Hall | Physics | 1964 |  | 94175 | Engineering, Physics and Chemistry | Engineering Birge | Packaged VAV, DX | 32 | 3013600 | 2410880 | 602720 | 0 | 0 | 80% | 20% | 0% | 0% |  | 2433.482 | 125 | 125 | 0 | 1.2371 | 0 | 3013600 | 2410880 | 602720 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1322 | Blum Hall | Mixed Use | 1914 |  | 23815 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 29.6 | 704924 | 610934.1333 | 93989.8667 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 569.2261 | 0 | 35.7225 | 35.7225 | 1.2371 | 44.1928 | 704924 | 563939.2 | 140984.8 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1231 | Boalt Hall | Classroom | 1966 |  | 277521 | Business and Law | Law East | Water-cooled chiller | 15.3 | 4246071.3 | 3821464.17 | 424607.13 | 0 | 0 | 90% | 10% | 0% | 0% |  | 3428.7026 | 0 | 277.521 | 277.521 | 0.585 | 162.3498 | 4246071.3 | 3821464.17 | 424607.13 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1230 | Bowles Hall | Residence | 1929 |  | 73700 | Engineering, Physics and Chemistry | Engineering Bowles | Packaged VAV, DX | 13.6 | 1002320 | 501160 | 501160 | 0 | 0 | 50% | 50% | 0% | 0% |  | 809.3734 | 0 | 51.59 | 51.59 | 1.2371 | 63.8227 | 1002320 | 501160 | 501160 | 0 | 0 | [5 empty] | 50% | 50% | 0% | 0%
1270 | California Hall | Admin | 1905 |  | 56343 | Engineering, Physics and Chemistry | Libraries Dwinelle | Packaged VAV, DX | 22.2 | 1250814.6 | 1125733.14 | 125081.46 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1010.0328 | 0 | 56.343 | 56.343 | 1.2371 | 69.7027 | 1250814.6 | 1125733.14 | 125081.46 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1271 | California Memorial Stadium | Athletic | 1923 |  | 261091 | Business and Law | Law East | Water-cooled chiller | 25.6 | 6683929.6 | 4010357.76 | 2673571.84 | 0 | 0 | 60% | 40% | 0% | 0% |  | 5397.2732 | 0 | 261.091 | 261.091 | 0.585 | 152.7382 | 6683929.6 | 4010357.76 | 2673571.84 | 0 | 0 | [5 empty] | 60% | 40% | 0% | 0%
1799 | Calvin Laboratory | Bioscience | 1963 |  | 33167 | Business and Law | Law East | Packaged VAV, DX | 35 | 1160845 | 650073.2 | 162518.3 | 0 | 348253.5 | 56% | 14% | 0% | 30% |  | 656.1676 | 85 | 85 | 0 | 1.2371 | 0 | 1160845 | 650073.2 | 162518.3 | 0 | 348253.5 | [5 empty] | 56% | 14% | 0% | 30%
1374 | Central Heating Plant | Mechanical | 1930 |  | 20385 | N/A | None | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0 | 20.385 | 20.385 | 1.2371 | 25.2186 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
1784 | Cesar E. Chavez Student Center | Admin | 1960 |  | 104016 | Lower Sproul offices | Lower Offices East | Packaged VAV, DX | 18.8 | 1955500.8 | 1759950.72 | 195550.08 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1579.0669 | 0 | 104.016 | 104.016 | 1.2371 | 128.6796 | 1955500.8 | 1759950.72 | 195550.08 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1233 | Cheit Hall | Classroom | 1995 |  | 32120 | Business and Law | Business | Packaged VAV, DX | 33.3 | 1069596 | 962636.4 | 106959.6 | 0 | 0 | 90% | 10% | 0% | 0% |  | 863.6988 | 0 | 32.12 | 32.12 | 1.2371 | 39.7361 | 1069596 | 962636.4 | 106959.6 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1325 | Cory Hall | Engineering | 1950 |  | 206054 | Engineering, Physics and Chemistry | Engineering Cory | Water-cooled chiller | 12.3 | 2534464.2 | 2027571.36 | 506892.84 | 0 | 0 | 80% | 20% | 0% | 0% |  | 2046.5798 | 150 | 150 | 0 | 0.585 | 0 | 2534464.2 | 2027571.36 | 506892.84 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1297 | David Gardner Stacks | Library | 1994 |  | 189425 | Engineering, Physics and Chemistry | Libraries Moffitt | Water-cooled chiller | 32 | 6061600 | 5455440 | 606160 | 0 | 0 | 90% | 10% | 0% | 0% |  | 4894.742 | 150 | 150 | 0 | 0.585 | 0 | 6061600 | 5455440 | 606160 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1323 | Davis Hall | Engineering | 1967 |  | 137806 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 32 | 4409792 | 3527833.6 | 881958.4 | 0 | 0 | 80% | 20% | 0% | 0% |  | 3560.907 | 75 | 75 | 0 | 1.2371 | 0 | 4409792 | 3527833.6 | 881958.4 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1301 | Doe Memorial Library | Library | 1917 |  | 166514 | Engineering, Physics and Chemistry | Libraries Moffitt | Water-cooled chiller | 32 | 5328448 | 4795603.2 | 532844.8 | 0 | 0 | 90% | 10% | 0% | 0% |  | 4302.7218 | 0 | 166.514 | 166.514 | 0.585 | 97.4107 | 5328448 | 4795603.2 | 532844.8 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1419 | Donner Laboratory | Chemistry | 1942 | 2030 | 53234 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 40 | 2129360 | 1341496.8 | 149055.2 | 0 | 638808 | 63% | 7% | 0% | 30% |  | 1203.6207 | 0 | 133.085 | 133.085 | 1.2371 | 164.6412 | 2129360 | 1341496.8 | 149055.2 | 0 | 638808 | [5 empty] | 63% | 7% | 0% | 30%
1227 | Durant Hall | Admin | 1911 |  | 21866 | Engineering, Physics and Chemistry | Libraries Dwinelle | Packaged VAV, DX | 16.1 | 352042.6 | 316838.34 | 35204.26 | 0 | 0 | 90% | 10% | 0% | 0% |  | 284.2744 | 0 | 21.866 | 21.866 | 1.2371 | 27.0507 | 352042.6 | 316838.34 | 35204.26 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1295 | Dwinelle Hall | Classroom | 1952 |  | 305268 | Engineering, Physics and Chemistry | Libraries Dwinelle | Water-cooled chiller | 32 | 9768576 | 8791718.4 | 976857.6 | 0 | 0 | 90% | 10% | 0% | 0% |  | 7888.1251 |  | 305.268 | 305.268 | 0.585 | 178.5818 | 9768576 | 8791718.4 | 976857.6 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1095 | Earl Warren Hall | Data Center | 2003 |  | 69032 | Biosciences | Biosciences North | Packaged VAV, DX | 32 | 2209024 | 1325414.4 | 883609.6 | 0 | 0 | 60% | 40% | 0% | 0% |  | 1783.7869 | 200 | 200 | 0 | 1.2371 | 0 | 2209024 | 1325414.4 | 883609.6 | 0 | 0 | [5 empty] | 60% | 40% | 0% | 0%
1318 | Edwards Stadium / Goldman Field | Athletic | 1932 | 2040 | 59326 | Lower Sproul offices | Edwards | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 60% | 40% | 0% | 0% |  | 0 | 0 | 59.326 | 59.326 | 1.2371 | 73.393 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 60% | 40% | 0% | 0%
1783 | Etcheverry Hall | Engineering | 1964 |  | 177281 | Engineering, Physics and Chemistry | Engineering North Halls | Water-cooled chiller | 32 | 5672992 | 4538393.6 | 1134598.4 | 0 | 0 | 80% | 20% | 0% | 0% |  | 4580.941 | 0 | 443.2025 | 443.2025 | 0.585 | 259.2735 | 5672992 | 4538393.6 | 1134598.4 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1790 | Evans Hall | Mixed Use | 1971 | 2025 | 270413 | Engineering, Physics and Chemistry | Engineering Evans | Water-cooled chiller | 35 | 9464455 | 8202527.6667 | 1261927.3333 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 7642.5474 | 0 | 405.6195 | 405.6195 | 0.585 | 237.2874 | 9464455 | 7571564 | 1892891 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1340 | Faculty Club | Admin | 1903 |  | 35483 | Business and Law | Business | Packaged VAV, DX | 28 | 993524 | 596114.4 | 397409.6 | 0 | 0 | 60% | 40% | 0% | 0% |  | 802.2706 | 0 | 35.483 | 35.483 | 1.2371 | 43.8965 | 0 | 0 | 0 | 0 | 0 | FLAG | FLAG | FLAG |  |  | 60% | 40% | 0% | 0%
1789 | Genetics & Plant Biology | Bioscience | 1990 |  | 26321 | Biosciences | Biosciences South | Packaged VAV, DX | 35 | 921235 | 515891.6 | 128972.9 | 0 | 276370.5 | 56% | 14% | 0% | 30% |  | 520.7281 | 0 | 65.8025 | 65.8025 | 1.2371 | 81.4052 | 921235 | 515891.6 | 128972.9 | 0 | 276370.5 | [5 empty] | 56% | 14% | 0% | 30%
1236 | Gerson Bakar Faculty Building | Admin | 1995 |  | 106295 | Business and Law | Business | Packaged VAV, DX | 32 | 3401440 | 3061296 | 340144 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2746.6628 | 0 | 106.295 | 106.295 | 1.2371 | 131.499 | 3401440 | 3061296 | 340144 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1355 | Giannini Hall | Classroom | 1930 |  | 68701 | Biosciences | Biosciences South | Packaged VAV, DX | 20.4 | 1401500.4 | 1261350.36 | 140150.04 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1131.7116 | 0 | 68.701 | 68.701 | 1.2371 | 84.9909 | 1401500.4 | 1261350.36 | 140150.04 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1410 | Giauque Laboratory | Chemistry | 1954 |  | 25996 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 32 | 831872 | 748684.8 | 83187.2 | 0 | 0 | 90% | 10% | 0% | 0% |  | 671.7366 |  | 64.99 | 64.99 | 1.2371 | 80.4 | 831872 | 748684.8 | 83187.2 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1356 | Gilman Hall | Chemistry | 1917 |  | 44182 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 20.9 | 923403.8 | 831063.42 | 92340.38 | 0 | 0 | 90% | 10% | 0% | 0% |  | 745.6486 | 180 | 180 | 0 | 1.2371 | 0 | 923403.8 | 831063.42 | 92340.38 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1424 | Hargrove Music Library | Library | 2004 |  | 29063 | Business and Law | Law West | Packaged VAV, DX | 24 | 697512 | 627760.8 | 69751.2 | 0 | 0 | 90% | 10% | 0% | 0% |  | 563.2409 | 0 | 29.063 | 29.063 | 1.2371 | 35.9542 | 697512 | 627760.8 | 69751.2 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1371 | Haviland Hall | Mixed Use | 1924 |  | 51020 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 24.1 | 1229582 | 1065637.7333 | 163944.2667 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 992.8875 | 0 | 76.53 | 76.53 | 1.2371 | 94.6763 | 1229582 | 983665.6 | 245916.4 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1267 | Hazardous Materials Facility | Mechanical | 1999 |  | 23432 | N/A | None | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0 | 23.432 | 23.432 | 1.2371 | 28.988 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
1097 | Hearst Field Annex | Mixed Use | 1999 |  | 34825 | Business and Law | Law West | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 0 | 0 | 52.2375 | 52.2375 | 1.2371 | 64.6237 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0% | FLAG | FLAG
1372 | Hearst Memorial Gymnasium | Athletic | 1927 |  | 124197 | Business and Law | Law West | Packaged VAV, DX | 32 | 3974304 | 2026895.04 | 1351263.36 | 0 | 596145.6 | 51% | 34% | 0% | 15% |  | 2727.8629 | 0 | 124.197 | 124.197 | 1.2371 | 153.6458 | 3974304 | 2026895.04 | 1351263.36 | 0 | 596145.6 | [5 empty] | 51% | 34% | 0% | 15%
1373 | Hearst Memorial Mining Building | Classroom | 1907 |  | 141461 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 32 | 4526752 | 4074076.8 | 452675.2 | 0 | 0 | 90% | 10% | 0% | 0% |  | 3655.3522 | 600 | 600 | 0 | 1.2371 | 0 | 4526752 | 4074076.8 | 452675.2 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1423 | Hertz Memorial Concert Hall | Classroom | 1958 |  | 30160 | Business and Law | Law Central | Packaged VAV, DX | 21.1 | 636376 | 572738.4 | 63637.6 | 0 | 0 | 90% | 10% | 0% | 0% |  | 513.8736 | 0 | 30.16 | 30.16 | 1.2371 | 37.3113 | 636376 | 572738.4 | 63637.6 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1375 | Hesse Hall | Engineering | 1924 | 2025 | 41363 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 21.3 | 881031.9 | 704825.52 | 176206.38 | 0 | 0 | 80% | 20% | 0% | 0% |  | 711.4333 | 0 | 103.4075 | 103.4075 | 1.2371 | 127.9268 | 881031.9 | 704825.52 | 176206.38 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1809 | Hildebrand Hall | Chemistry | 1966 |  | 128126 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 32 | 4100032 | 1476011.52 | 164001.28 | 1640012.8 | 820006.4 | 36% | 4% | 40% | 20% |  | 1324.3103 | 525 | 525 | 0 | 1.2371 | 0 | 4100032 | 1476011.52 | 164001.28 | 1640012.8 | 820006.4 | [5 empty] | 36% | 4% | 40% | 20%
1376 | Hilgard Hall | Bioscience | 1917 |  | 77055 | Biosciences | Biosciences South | Packaged VAV, DX | 32 | 2465760 | 1972608 | 493152 | 0 | 0 | 80% | 20% | 0% | 0% |  | 1991.1012 | 0 | 192.6375 | 192.6375 | 1.2371 | 238.3144 | 2465760 | 1972608 | 493152 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0%
1390 | International House | Residence | 1930 |  | 185200 | Business and Law | Law East | Water-cooled chiller | 32 | 5926400 | 2963200 | 2963200 | 0 | 0 | 50% | 50% | 0% | 0% |  | 4785.568 | 0 | 129.64 | 129.64 | 0.585 | 75.8394 | 5926400 | 2963200 | 2963200 | 0 | 0 | [5 empty] | 50% | 50% | 0% | 0%
1032 | Jacobs | Engineering | 2015 |  | 24000 | Engineering, Physics and Chemistry | Engineering North Halls | Packaged VAV, DX | 35.94 | 862560 | 483033.6 | 120758.4 | 0 | 258768 | 56% | 14% | 0% | 30% |  | 487.562 | 0 | 60 | 60 | 1.2371 | 74.2268 | 0
1796 | Koshland Hall | Bioscience | 1990 |  | 153700 | Biosciences | Biosciences North | Water-cooled chiller | 32 | 4918400 | 2754304 | 688576 | 0 | 1475520 | 56% | 14% | 0% | 30% |  | 2780.1256 | 720 | 720 | 0 | 0.585 | 0 | 4918400 | 2754304 | 688576 | 0 | 1475520 | [5 empty] | 56% | 14% | 0% | 30%
1486 | Kroeber Hall | Classroom | 1959 |  | 117814 | Business and Law | Law Central | Packaged VAV, DX | 8.2 | 966074.8 | 869467.32 | 96607.48 | 0 | 0 | 90% | 10% | 0% | 0% |  | 780.1054 | 0 | 117.814 | 117.814 | 1.2371 | 145.7493 | 966074.8 | 869467.32 | 96607.48 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1782 | Latimer Hall | Chemistry | 1963 |  | 182943 | Engineering, Physics and Chemistry | Engineering Lewis | Water-cooled chiller | 45 | 8232435 | 7409191.5 | 823243.5 | 8327450 | 0 | 90% | 10% | 0% | 0% |  | 6647.6913 | 500 | 500 | 0 | 0.585 | 0 | 8232435 | 7409191.5 | 823243.5 | 8327450 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1405 | LeConte Hall | Mixed Use | 1924 |  | 148032 | Engineering, Physics and Chemistry | Engineering Birge | Packaged VAV, DX | 32 | 4737024 | 4105420.8 | 631603.2 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 3825.1469 | 100 | 100 | 0 | 1.2371 | 0 | 4737024 | 3789619.2 | 947404.8 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1292 | Lewis Hall | Chemistry | 1948 |  | 68146 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 26.9 | 1833127.4 | 1154870.262 | 128318.918 | 0 | 549938.22 | 63% | 7% | 0% | 30% |  | 1036.1753 | 200 | 200 | 0 | 1.2371 | 0 | 1833127.4 | 1154870.262 | 128318.918 | 0 | 549938.22 | [5 empty] | 63% | 7% | 0% | 30%
1444 | Li Ka Shing Center | Bioscience | 2011 |  | 220703 | Biosciences | Biosciences South | Water-cooled chiller | 40 | 8828120 | 4943747.2 | 1235936.8 | 0 | 2648436 | 56% | 14% | 0% | 30% |  | 4990.0948 | 1220 | 1220 | 0 | 0.585 | 0 | 8828120 | 4943747.2 | 1235936.8 | 0 | 2648436 | [5 empty] | 56% | 14% | 0% | 30%
1225 | Life Sciences Addition | Bioscience | 1988 |  | 201824 | Engineering, Physics and Chemistry | Life Sciences | Water-cooled chiller | 32 | 6458368 | 3616686.08 | 904171.52 | 0 | 1937510.4 | 56% | 14% | 0% | 30% |  | 3650.5925 | 1200 | 1200 | 0 | 0.585 | 0 | 6458368 | 3616686.08 | 904171.52 | 0 | 1937510.4 | [5 empty] | 56% | 14% | 0% | 30%
1762 | McCone Hall | Mixed Use | 1961 |  | 123612 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 32 | 3955584 | 3428172.8 | 527411.2 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 3194.1341 | 95 | 95 | 0 | 1.2371 | 0 | 3955584 | 3164467.2 | 791116.8 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1321 | McLaughlin Hall | Admin | 1931 |  | 49388 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 32 | 1580416 | 1422374.4 | 158041.6 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1276.1859 | 0 | 49.388 | 49.388 | 1.2371 | 61.0986 | 1580416 | 1422374.4 | 158041.6 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1302F | Minor Hall | Mixed Use | 1941 |  | 46204 | Business and Law | Business | Packaged VAV, DX | 22.4 | 1034969.6 | 717578.9227 | 110396.7573 | 0 | 206993.92 | 69.33% | 10.67% | 0% | 20% |  | 668.5904 | 0 | 69.306 | 69.306 | 1.2371 | 85.7394 | 1034969.6 | 662380.544 | 165595.136 | 0 | 206993.92 |  | FLAG | FLAG |  |  | 64% | 16% | 0% | 20% | FLAG | FLAG
1302 | Minor Hall Addition | Mixed Use | 1978 |  | 55516 | Business and Law | Business | Packaged VAV, DX | 32 | 1776512 | 1539643.7333 | 236868.2667 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 1434.5334 | 500 | 500 | 0 | 1.2371 | 0 | 1776512 | 1421209.6 | 355302.4 | 0 | 0 |  | FLAG | FLAG |  |  | 80% | 20% | 0% | 0% | FLAG | FLAG
1791 | MLK, Jr. Student Union | Admin | 1961 |  | 102901 | Lower Sproul offices | Lower Offices East | Packaged VAV, DX | 32 | 3292832 | 2963548.8 | 329283.2 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2658.9618 | 0 | 102.901 | 102.901 | 1.2371 | 127.3002 | 3292832 | 2963548.8 | 329283.2 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1299 | Moffitt Undergraduate Library | Library | 1970 |  | 130581 | Engineering, Physics and Chemistry | Libraries Moffitt | Packaged VAV, DX | 31.7 | 4139417.7 | 1490190.372 | 165576.708 | 2483650.62 | 0 | 36% | 4% | 60% | 0% |  | 1337.0319 | 260 | 260 | 0 | 1.2371 | 0 | 4139417.7 | 1490190.372 | 165576.708 | 2483650.62 | 0 | [5 empty] | 36% | 4% | 60% | 0%
1382 | Morgan Hall | Mixed Use | 1953 |  | 56637 | Biosciences | Biosciences South | Packaged VAV, DX | 32 | 1812384 | 1256586.24 | 193320.96 | 0 | 362476.8 | 69.33% | 10.67% | 0% | 20% |  | 1170.8001 | 0 | 84.9555 | 84.9555 | 1.2371 | 105.0996 | 1812384 | 1159925.76 | 289981.44 | 0 | 362476.8 |  | FLAG | FLAG |  |  | 64% | 16% | 0% | 20% | FLAG | FLAG
1422 | Morrison Hall | Classroom | 1958 |  | 40706 | Business and Law | Law Central | Packaged VAV, DX | 29 | 1180474 | 1062426.6 | 118047.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 953.2328 | 0 | 40.706 | 40.706 | 1.2371 | 50.3579 | 1180474 | 1062426.6 | 118047.4 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1324 | Moses Hall | Classroom | 1931 |  | 40835 | Engineering, Physics and Chemistry | Libraries Moses | Packaged VAV, DX | 30.2 | 1233217 | 1109895.3 | 123321.7 | 0 | 0 | 90% | 10% | 0% | 0% |  | 995.8227 | 0 | 40.835 | 40.835 | 1.2371 | 50.5175 | 1233217 | 1109895.3 | 123321.7 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1346 | Mulford Hall | Classroom | 1948 |  | 93420 | Biosciences | Biosciences South | Packaged VAV, DX | 24 | 2242080 | 1614297.6 | 179366.4 | 0 | 448416 | 72% | 8% | 0% | 20% |  | 1448.3837 | 0 | 93.42 | 93.42 | 1.2371 | 115.5711 | 2242080 | 1614297.6 | 179366.4 | 0 | 448416 | [5 empty] | 72% | 8% | 0% | 20%
1206 | North Gate Hall | Classroom | 1906 |  | 23533 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 16.9 | 397707.7 | 357936.93 | 39770.77 | 0 | 0 | 90% | 10% | 0% | 0% |  | 321.149 | 0 | 23.533 | 23.533 | 1.2371 | 29.113 | 397707.7 | 357936.93 | 39770.77 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1229 | Northwest Animal Facility | Bioscience | 1991 |  | 52845 | Biosciences | Biosciences North | Packaged VAV, DX | 40 | 2113800 | 1183728 | 295932 | 0 | 634140 | 56% | 14% | 0% | 30% |  | 1194.8254 |  | 132.1125 | 132.1125 | 1.2371 | 163.4381 | 2113800 | 1183728 | 295932 | 0 | 634140 | [5 empty] | 56% | 14% | 0% | 30%
1377 | O'Brien Hall | Classroom | 1959 | 2025 | 41297 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 22 | 908534 | 817680.6 | 90853.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 733.6412 | 0 | 41.297 | 41.297 | 1.2371 | 51.0891 | 908534 | 817680.6 | 90853.4 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1801 | Pimentel Hall | Classroom | 1964 |  | 14524 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 32 | 464768 | 418291.2 | 46476.8 | 0 | 0 | 90% | 10% | 0% | 0% |  | 375.3002 | 0 | 14.524 | 14.524 | 1.2371 | 17.9678 | 464768 | 418291.2 | 46476.8 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1365 | Recreational Sports Facility | Athletic | 1984 |  | 187982 | Lower Sproul offices | Edwards | Water-cooled chiller | 32 | 6015424 | 3609254.4 | 2406169.6 | 0 | 0 | 60% | 40% | 0% | 0% |  | 4857.4549 | 0 | 187.982 | 187.982 | 0.585 | 109.9695 | 6015424 | 3609254.4 | 2406169.6 | 0 | 0 | [5 empty] | 60% | 40% | 0% | 0%
1391 | Simon Hall | Classroom | 1966 |  | 36180 | Business and Law | Law East | Packaged VAV, DX | 32 | 1157760 | 1041984 | 115776 | 0 | 0 | 90% | 10% | 0% | 0% |  | 934.8912 | 0 | 36.18 | 36.18 | 1.2371 | 44.7588 | 1157760 | 1041984 | 115776 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1277 | Simpson Student-Athlete High Performance Center | Athletic | 2011 |  | 139682 | Business and Law | Law East | Packaged VAV, DX | 6 | 838092 | 502855.2 | 335236.8 | 0 | 0 | 60% | 40% | 0% | 0% |  | 676.7593 | 0 | 139.682 | 139.682 | 1.2371 | 172.8025 | 0 | 0 | 0 | 0 | 0 | FLAG | FLAG | FLAG |  |  | 60% | 40% | 0% | 0%
1237 | Soda Hall | Mixed Use | 1994 |  | 109588 | Engineering, Physics and Chemistry | Engineering North Halls | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 0 | 470 | 470 | 0 | 1.2371 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 80% | 20% | 0% | 0% | FLAG | FLAG
1484 | South Hall | Classroom | 1873 |  | 30401 | Engineering, Physics and Chemistry | Libraries Dwinelle | Packaged VAV, DX | 14.5 | 440814.5 | 396733.05 | 44081.45 | 0 | 0 | 90% | 10% | 0% | 0% |  | 355.9577 | 0 | 30.401 | 30.401 | 1.2371 | 37.6095 | 440814.5 | 396733.05 | 44081.45 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1210 | Sproul Hall | Admin | 1941 |  | 110919 | Business and Law | Law West | Packaged VAV, DX | 15.3 | 1697060.7 | 1527354.63 | 169706.07 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1370.3765 | 0 | 110.919 | 110.919 | 1.2371 | 137.2194 | 1697060.7 | 1527354.63 | 169706.07 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1149 | Stanley Hall | Chemistry | 2006 |  | 304333 | Engineering, Physics and Chemistry | Engineering Evans | Water-cooled chiller | 32 | 9738656 | 3505916.16 | 389546.24 | 12229760 | 1947731.2 | 36% | 4% | 40% | 20% |  | 3145.5859 | 1800 | 1800 | 0 | 0.585 | 0 | 9738656 | 3505916.16 | 389546.24 | 12229760 | 1947731.2 | [5 empty] | 36% | 4% | 40% | 20%
1150 | Starr East Asian Library | Library | 2007 |  | 65860 | Engineering, Physics and Chemistry | Engineering Evans | Packaged VAV, DX | 32 | 2107520 | 758707.2 | 84300.8 | 1264512 | 0 | 36% | 4% | 60% | 0% |  | 680.729 | 250 | 250 | 0 | 1.2371 | 0 | 2107520 | 758707.2 | 84300.8 | 1264512 | 0 | [5 empty] | 36% | 4% | 60% | 0%
1661 | Steam Tunnel | mechanical | 1930 |  | 13720 | N/A | None | Packaged VAV, DX | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0% | 0% | 0% | FLAG | 0 | 0 | 13.72 | 13.72 | 1.2371 | 16.9732 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0% | 0% | 0% | 0%
1488 | Stephens Hall | Classroom | 1923 |  | 58733 | Engineering, Physics and Chemistry | Libraries Moses | Packaged VAV, DX | 18 | 1057194 | 951474.6 | 105719.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 853.6842 | 0 | 58.733 | 58.733 | 1.2371 | 72.6594 | 1057194 | 951474.6 | 105719.4 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1495 | Stern Hall | Residence | 1942 |  | 86959 | Engineering, Physics and Chemistry | Engineering Bowles | Packaged VAV, DX | 16.7 | 1452215.3 | 726107.65 | 726107.65 | 0 | 0 | 50% | 50% | 0% | 0% |  | 1172.6639 | 0 | 60.8713 | 60.8713 | 1.2371 | 75.3047 | 1452215.3 | 726107.65 | 726107.65 | 0 | 0 | [5 empty] | 50% | 50% | 0% | 0%
1152 | Sutardja Dai Hall | Engineering | 2009 |  | 154706 | Engineering, Physics and Chemistry | Engineering Cory | Water-cooled chiller | 90 | 13923540 | 4455532.8 | 1113883.2 | 11509050 | 0 | 32% | 8% | 60% | 0% |  | 4497.3034 | 1200 | 1200 | 0 | 0.585 | 0 | 13923540 | 4455532.8 | 1113883.2 | 11509050 | 0 | [5 empty] | 32% | 8% | 60% | 0%
1808 | Tan Hall | Chemistry | 1996 |  | 116121 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 32 | 3715872 | 2340999.36 | 260111.04 | 0 | 1114761.6 | 63% | 7% | 0% | 30% |  | 2100.3966 | 300 | 300 | 0 | 1.2371 | 0 | 3715872 | 2340999.36 | 260111.04 | 0 | 1114761.6 | [5 empty] | 63% | 7% | 0% | 30%
1594 | University Hall | Admin | 1959 |  | 150887 | Biosciences | University | Water-cooled chiller | 32 | 4828384 | 4345545.6 | 482838.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 3898.9201 | 0 | 150.887 | 150.887 | 0.585 | 88.2689 | 4828384 | 4345545.6 | 482838.4 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1439 | University House | residence | 1911 |  | 18112 | Biosciences | Biosciences North | Packaged VAV, DX | 25.4 | 460044.8 | 230022.4 | 230022.4 | 0 | 0 | 50% | 50% | 0% | 0% |  | 371.4862 | 0 | 12.6784 | 12.6784 | 1.2371 | 15.6846 | 460044.8 | 230022.4 | 230022.4 | 0 | 0 | [5 empty] | 50% | 50% | 0% | 0%
1406 | Valley Life Sciences Building | Bioscience | 1930 |  | 420885 | Engineering, Physics and Chemistry | Life Sciences | Water-cooled chiller | 32 | 13468320 | 7542259.2 | 1885564.8 | 0 | 4040496 | 56% | 14% | 0% | 30% |  | 7612.9679 | 850 | 850 | 0 | 0.585 | 0 | 13468320 | 7542259.2 | 1885564.8 | 0 | 4040496 | [5 empty] | 56% | 14% | 0% | 30%
1234 | Walter A. Haas Student Services Building | Admin | 1995 |  | 95712 | Business and Law | Business | Packaged VAV, DX | 32 | 3062784 | 2756505.6 | 306278.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2473.1981 | 200 | 200 | 0 | 1.2371 | 0 | 3062784 | 2756505.6 | 306278.4 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
1360 | Walter A. Haas, Jr. Pavilion | Athletic | 1933 |  | 238065 | Lower Sproul offices | Edwards | Water-cooled chiller | 32 | 7618080 | 4570848 | 3047232 | 0 | 0 | 60% | 40% | 0% | 0% |  | 6151.5996 | 0 | 238.065 | 238.065 | 0.585 | 139.268 | 7618080 | 4570848 | 3047232 | 0 | 0 | [5 empty] | 60% | 40% | 0% | 0%
1202 | Wellman Hall | Classroom | 1912 |  | 43910 | Biosciences | Biosciences South | Packaged VAV, DX | 32 | 1405120 | 1011686.4 | 112409.6 | 0 | 281024 | 72% | 8% | 0% | 20% |  | 907.7075 | 0 | 43.91 | 43.91 | 1.2371 | 54.3216 | 1405120 | 1011686.4 | 112409.6 | 0 | 281024 | [5 empty] | 72% | 8% | 0% | 20%
1552 | Wheeler Hall | Mixed Use | 1917 |  | 139436 | Engineering, Physics and Chemistry | Libraries Dwinelle | Packaged VAV, DX | 21.4 | 2983930.4 | 2586073.0133 | 397857.3867 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 2409.5238 | 0 | 209.154 | 209.154 | 1.2371 | 258.7472 | 2983930.4 | 2685537.36 | 298393.04 | 0 | 0 |  | FLAG | FLAG |  |  | 90% | 10% | 0% | 0% | FLAG | FLAG
1553 | Women's Faculty Club | Admin | 1923 |  | 18474 | Business and Law | Business | Packaged VAV, DX | 28 | 517272 | 465544.8 | 51727.2 | 0 | 0 | 90% | 10% | 0% | 0% |  | 417.6971 | 0 | 18.474 | 18.474 | 1.2371 | 22.8544 | 0 | 0 | 0 | 0 | 0 | FLAG | FLAG | FLAG |  |  | 90% | 10% | 0% | 0%
1797 | Wurster Hall | Classroom | 1964 |  | 222434 | Business and Law | Law Central | Water-cooled chiller | 5 | 1112170 | 1000953 | 111217 | 0 | 0 | 90% | 10% | 0% | 0% |  | 898.0773 | 0 | 222.434 | 222.434 | 0.585 | 130.1239 | 0 | 0 | 0 | 0 | 0 | FLAG | FLAG | FLAG |  |  | 90% | 10% | 0% | 0%
1802 | Zellerbach Hall | Auditorium | 1968 |  | 153118 | Lower Sproul offices | Lower Offices East | Water-cooled chiller | 32 | 4899776 | 4409798.4 | 489977.6 | 0 | 0 | 90% | 10% | 0% | 0% |  | 3956.5691 | 0 | 153.118 | 153.118 | 0.585 | 89.574 | 4899776 | 4409798.4 | 489977.6 | 0 | 0 | [5 empty] | 90% | 10% | 0% | 0%
New Buildings
1325 (N) | Cory Hall (N) | Engineering | 2028 |  | 200000 | Engineering, Physics and Chemistry | Engineering Cory | Water-cooled chiller | 35.94 | 7188000 | 5750400 | 1437600 | 0 | 0 | 80% | 20% | 0% | 0% |  | 5804.31 | 0 | 500 | 500 | 0.585 | 292.5 | 0
1323 (N) | Davis Hall (N) | Engineering | 2025 |  | 150000 | Engineering, Physics and Chemistry | Engineering Cory | Water-cooled chiller | 35.94 | 5391000 | 4312800 | 1078200 | 0 | 0 | 80% | 20% | 0% | 0% |  | 4353.2325 | 0 | 375 | 375 | 0.585 | 219.375 | 0
1419 (N) | Donner Laboratory (N) | Chemistry | 2028 |  | 100000 | Engineering, Physics and Chemistry | Engineering Cory | Packaged VAV, DX | 35.94 | 3594000 | 3234600 | 359400 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2902.155 | 0 | 250 | 250 | 1.2371 | 309.2784 | 0
1318 (N) | Edwards Stadium / Goldman Field New Quad (N) | Engineering | 2040 |  | 1500000 | Lower Sproul offices | Edwards | Water-cooled chiller | 35.94 | 53910000 | 38815200 | 9703800 | 0 | 5391000 | 72% | 18% | 0% | 10% |  | 39179.0925 | 0 | 3750 | 3750 | 0.585 | 2193.75 | 0
1790 (N) | Evans Hall (N) | Classroom | 2030 |  | 165000 | Engineering, Physics and Chemistry | Engineering Evans | Water-cooled chiller | 10.1 | 1666500 | 1049895 | 116655 | 0 | 499950 | 63% | 7% | 0% | 30% |  | 941.9891 | 0 | 165 | 165 | 0.585 | 96.525 | 0
1375 (N) | Hesse/O'Brien (N) | Engineering | 2025 |  | 225000 | Engineering, Physics and Chemistry | Engineering Evans | Water-cooled chiller | 35.94 | 8086500 | 4528440 | 1132110 | 0 | 2425950 | 56% | 14% | 0% | 30% |  | 4570.8941 | 0 | 562.5 | 562.5 | 0.585 | 329.0625 | 0
1292 (N) | Lewis Hall (N) | Chemistry | 2040 |  | 87500 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 35.94 | 3144750 | 2830275 | 314475 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2539.3856 | 0 | 218.75 | 218.75 | 1.2371 | 270.6186 | 0
CAAN? | Lewis Hall Addition | Chemistry | 2028 |  | 90000 | Engineering, Physics and Chemistry | Engineering Lewis | Packaged VAV, DX | 35.94 | 3234600 | 2911140 | 323460 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2611.9395 | 0 | 225 | 225 | 1.2371 | 278.3505 | 0
1785 | Oxford Tract | Residence | 2025 |  | 1050000 | Biosciences | Oxford Tract | Water-cooled chiller | 14.14 | 14847000 | 7423500 | 7423500 | 0 | 0 | 50% | 50% | 0% | 0% |  | 11988.9525 | 0 | 735 | 735 | 0.585 | 429.975 | 0
1601 | Peoples Park | Residence | 2023 |  | 432000 | Lower Sproul offices | Peoples Park | Water-cooled chiller | 14.14 | 6108480 | 3054240 | 3054240 | 0 | 0 | 50% | 50% | 0% | 0% |  | 4932.5976 | 0 | 302.4 | 302.4 | 0.585 | 176.904 | 0
1774 (N) | Tolman Hall (N) (Climate Science Building) | Bioscience | 2025 |  | 292500 | Biosciences | Biosciences North | Water-cooled chiller | 41.44 | 12121200 | 9696960 | 2424240 | 0 | 0 | 80% | 20% | 0% | 0% |  | 9787.869 | 0 | 731.25 | 731.25 | 0.585 | 427.7812 | 0
Electric Only Buildings
1526 | Gateway Site | Residence | 2023 |  | 252000 |  |  | Water-cooled chiller | 14.14 | 3563280 | 1781640 | 1781640 | 0 | 0 | 50% | 50% | 0% | 0% |  | 2877.3486 | 0 | 176.4 | 176.4 | 0.585 | 103.194 | 0
1037 | Berkeley Way West | Admin | 2018 |  | 260000 |  |  | Water-cooled chiller | 10.1 | 2626000 | 2363400 | 262600 | 0 | 0 | 90% | 10% | 0% | 0% |  | 2120.495 | 0 | 260 | 260 | 0.585 | 152.1 | 0
1810A | Silver Space Sciences Lab | Physics |  |  | 28629 |  |  | Packaged VAV, DX | 35.94 | 1028926.26 | 823141.008 | 205785.252 | 0 | 0 | 80% | 20% | 0% | 0% |  | 830.858 | 0 | 71.5725 | 71.5725 | 1.2371 | 88.5433 | 0
1813 | Silver Space Sciences Addition | Physics |  |  | 24392 |  |  | Packaged VAV, DX | 35.94 | 876648.48 | 701318.784 | 175329.696 | 0 | 0 | 80% | 20% | 0% | 0% |  | 707.8936 | 0 | 60.98 | 60.98 | 1.2371 | 75.4392 | 0
CAAN? | MSRI | Classroom | [5 empty] | Packaged Single Zone, DX | 10.1 | 0 | 0 | 0 | 0 | 0 | 90% | 10% | 0% | 0% |  | 0 | 0 | 0 | 0 | 1.2 | 0 | 0
1781 | Botanical Gardens | Bioscience | 1959 |  | 3964 |  |  | Packaged Single Zone, DX | 41.44 | 164268.16 | 131414.528 | 32853.632 | 0 | 0 | 80% | 20% | 0% | 0% |  | 132.6465 | 0 | 9.91 | 9.91 | 1.2 | 11.892 | 0
1437 | Strawberry Center | Athletic | 1928 | 2030 | 7600 |  |  | Packaged Single Zone, DX | 10.1 | 76760 | 46056 | 30704 | 0 | 0 | 60% | 40% | 0% | 0% |  | 61.9837 | 0 | 7.6 | 7.6 | 1.2 | 9.12
CAAN? | Crossroads | Residence | [5 empty] | Packaged Single Zone, DX | 14.14 | 0 | 0 | 0 | 0 | 0 | 50% | 50% | 0% | 0% |  | 0 | 0 | 0 | 0 | 1.2 | 0
1017 | BAM PFA | Other | 2015 |  | 82670 |  |  | Packaged VAV, DX | 18.7133 | 1547031.2667 | 1340760.4311 | 206270.8356 | 0 | 0 | 86.67% | 13.33% | 0% | 0% |  | 1249.2277 | 0 | 124.005 | 124.005 | 1.2371 | 153.4082
2010 | Clark Kerr Campus 23 - Archives | Residence | 1952 | 2030 | 29861 |  |  | Packaged VAV, DX | 14.14 | 422234.54 | 211117.27 | 211117.27 | 0 | 0 | 50% | 50% | 0% | 0% |  | 340.9544 | 0 | 20.9027 | 20.9027 | 1.2371 | 25.859
1022 | Energy Biosciences Building | Bioscience | 2012 |  | 120694 |  |  | Packaged VAV, DX | 41.44 | 5001559.36 | 4001247.488 | 1000311.872 | 0 | 0 | 80% | 20% | 0% | 0% |  | 4038.7592 | 0 | 301.735 | 301.735 | 1.2371 | 373.2804
1800 | Lawrence Hall of Science | Classroom | 1968 |  | 128540 |  |  | Packaged VAV, DX | 10.1 | 1298254 | 1168428.6 | 129825.4 | 0 | 0 | 90% | 10% | 0% | 0% |  | 1048.3401 | 0 | 128.54 | 128.54 | 1.2371 | 159.0186
1286 | Tang Center | Admin | 1993 |  | 75228 |  |  | Packaged VAV, DX | 10.1 | 759802.8 | 683822.52 | 75980.28 | 0 | 0 | 90% | 10% | 0% | 0% |  | 613.5408 | 0 | 75.228 | 75.228 | 1.2371 | 93.0656
1033 | Chou Hall | Classroom | 2018 |  | 80000 |  |  | Packaged VAV, DX | 10.1 | 808000 | 727200 | 80800 | 0 | 0 | 90% | 10% | 0% | 0% |  | 652.46 | 0 | 80 | 80 | 1.2371 | 98.9691
1787 | Upper Hearst | Residence | 2021 |  | 54000 |  |  | Packaged VAV, DX | 14.14 | 763560 | 381780 | 381780 | 0 | 0 | 50% | 50% | 0% | 0% |  | 616.5747 | 0 | 37.8 | 37.8 | 1.2371 | 46.7629
1520 | Bakar Bioenginuity | Bioscience | 1970 |  | 102794 |  |  | Packaged VAV, DX | 41.44 | 4259783.36 | 3407826.688 | 851956.672 | 0 | 0 | 80% | 20% | 0% | 0% |  | 3439.7751 | 0 | 256.985 | 256.985 | 1.2371 | 317.9196 | 1932527.2 | 695709.792 | 77301.088 | 1159516.32 | 0
[9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A |  | #N/A
[9 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A |  | #N/A
Totals
Note on L12: Erica Levine: From Syska Hennessey Fire and Ice Study
Note on L40: Erica Levine: Not available from Fire & Ice study; use condensate derived enthalpy from 2015 study
Note on L49: Erica Levine: Not available from Fire & Ice study; use condensate derived enthalpy from 2015 study
Note on P60: Erica Levine: 8585 lbs/hr from Fire & Ice study
Note on L81: Erica Levine: Not available from Fire & Ice study; use condensate derived enthalpy from 2015 study
Note on P85: Erica Levine: 12608 lbs/hr from Fire & Ice study
Note on P90: Erica Levine: 11865 lbs/hr from Fire & Ice study
Note on L99: Erica Levine: Not available from Fire & Ice study; use condensate derived enthalpy from 2015 study
Note on L100: Erica Levine: Not available from Fire & Ice study; use condensate derived enthalpy from 2015 study
Note on B102: Erica Levine: Update with info received from Raphael

## Outputs
Client | UC Berkeley |  |  |  |  | Input
Project | Campus energy study update |  |  |  |  | Lookup
Job Number | 267147 |  |  |  |  | Calculation
Output
Check
Outputs
Peak Loads by Node
Node | Building Area (sqft) | Peak Load |  | Check |  | Diversity |  | Heat Recovery
|  | Heating (kBtu/h) | Cooling (tons) | Heating (Btuh/sqft) | Cooling (sqft/ton) | Heating (%) | Cooling (%) | kBtu/h | MMBtu/y
Biosciences | 2459914 | 38695.1506 | 4418.7867 | 15.7303 | 556.6944 | 85% | 95%
Business and Law | 2225965 | 29627.3471 | 2670.9483 | 13.3099 | 833.3988 | 85% | 95%
Engineering, Physics and Chemistry | 5941627 | 105758.0928 | 13373.2244 | 17.7995 | 444.2928 | 85% | 95%
Libraries | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 85% | 95%
Lower Sproul offices | 2792734 | 53997.9225 | 4667.4773 | 19.3351 | 598.3391 | 85% | 95%
Campus | 13420240 | 214662.1299 | 23807.7821 | 15.9954 | 563.6913 | 80% | 90%
Electrical Loads Calculation
Node | Peak Load
| Absorption (tons) | Process Steam (Btu/hr) | Existing Cooling (tons) | Absorption (MW) | Process Steam (MW) | Existing Cooling (MW) | Process Steam (lb/hr) | Building Cooling (MW)
Biosciences | 0 | 6952856.9 | 2340 | 0 | 2.0378 | 2.925 | 7167.8937 | 1.8049
Business and Law | 0 | 1151393.02 | 785 | 0 | 0.33745 | 0.98125 | 1187.0031 | 1.8002
Engineering, Physics and Chemistry | 3121.203 | 14233919.82 | 6158.797 | 1.5606 | 4.1717 | 7.6985 | 14674.1441 | 4.0283
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lower Sproul offices | 0 | 5391000 | 0 | 0 | 1.58 | 0 | 5557.732 | 3.0578
Campus | 3121.203 | 27729169.74 | 9283.797 | 1.5606 | 8.127 | 11.6047 | 28586.7729 | 10.6912
Peak Loads by Cluster
Cluster | Building Area (sqft) | Peak Load |  | Check |  | Year Transferred | Phase
|  | Heating (kBtu/h) | Cooling (tons) |  |  |  | Node
Biosciences North | 672280 | 17475.3071 | 1996.0409 | 25.9941 | 336.8067 | 2025 | Biosciences
Biosciences South | 586747 | 12160.527 | 1769.4265 | 20.7253 | 331.6029 | 2030 | Biosciences
Business | 389804 | 9406.6512 | 961.678 | 24.1317 | 405.3373 | 2035 | Business and Law
Edwards | 1985373 | 50188.147 | 4235.373 | 25.279 | 468.7599 | 2040 | Lower Sproul Offices
Engineering Birge | 242207 | 6258.6289 | 225 | 25.84 | 1076.4756 | 2040 | Engineering, Physics and Chemistry
Engineering Bowles | 160659 | 1982.0373 | 112.4613 | 12.3369 | 1428.5714 | 2045 | Engineering, Physics and Chemistry
Engineering Cory | 1238563 | 30152.9672 | 3390.2945 | 24.3451 | 365.3261 | 2035 | Engineering, Physics and Chemistry
Engineering Evans | 1337286 | 23890.0274 | 3548.742 | 17.8646 | 376.8338 | 2030 | Engineering, Physics and Chemistry
Engineering Lewis | 757538 | 18052.584 | 2228.264 | 23.8306 | 339.9678 | 2040 | Engineering, Physics and Chemistry
Engineering North Halls | 310869 | 5068.5031 | 973.2025 | 16.3043 | 319.4289 | 2035 | Engineering, Physics and Chemistry
Law Central | 411114 | 3145.2891 | 411.114 | 7.6506 | 1000 | 2040 | Business and Law
Law East | 932841 | 15879.3619 | 929.114 | 17.0226 | 1004.0113 | 2035 | Business and Law
Law West | 492206 | 6424.4003 | 509.6185 | 13.0523 | 965.8323 | 2040 | Business and Law
Libraries Moses | 99568 | 1849.5069 | 99.568 | 18.5753 | 1000 | 2045 | Engineering, Physics and Chemistry
Libraries Moffitt | 618914 | 13955.5566 | 826.514 | 22.5485 | 748.8246 | 2030 | Engineering, Physics and Chemistry
Libraries Dwinelle | 553314 | 11947.9138 | 623.032 | 21.5934 | 888.0988 | 2045 | Engineering, Physics and Chemistry
Life Sciences | 622709 | 11263.5604 | 2050 | 18.088 | 303.7605 | 2045 | Engineering, Physics and Chemistry
Lower Offices East | 375361 | 8406.2231 | 375.361 | 22.395 | 1000 | 2045 | Lower Sproul offices
None | 57537 | 0 | 57.537 | 0 | 1000 | 2500 | N/A
Oxford Tract | 1050000 | 11988.9525 | 735 | 11.4181 | 1428.5714 | 2025 | Biosciences
Peoples Park | 432000 | 4932.5976 | 302.4 | 11.4181 | 1428.5714 | 2045 | Lower Sproul offices
University | 150887 | 3898.9201 | 150.887 | 25.84 | 1000 | 2030 | Biosciences
| 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0 | 0 | 0 | #DIV/0! | #DIV/0!
Cumulative Peak Loads by Phase
Phase |  | Building Area (sqft) | Peak Load |  | Check |  | Diversity |  | Heat Recovery
Node | Year Transferred |  | Heating (kBtu/h) | Cooling (tons) |  |  | Heating (%) | Cooling (%) | kBtu/h | kBtu/y
Biosciences | 2025 | 1722280 | 28874.9744 | 2703.7305 | 16.7656 | 637.0014 | 98% | 99%
Biosciences | 2030 | 2459914 | 40060.8618 | 4604.8409 | 16.2855 | 534.2017 | 88% | 99%
Biosciences | 2035 | 2459914 | 40060.8618 | 4604.8409 | 16.2855 | 534.2017 | 88% | 99%
Biosciences | 2040 | 2459914 | 40060.8618 | 4604.8409 | 16.2855 | 534.2017 | 88% | 99%
Biosciences | 2045 | 2459914 | 40060.8618 | 4604.8409 | 16.2855 | 534.2017 | 88% | 99%
Business and Law | 2025 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Business and Law | 2030 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Business and Law | 2035 | 1322645 | 20987.3909 | 1871.8841 | 15.8677 | 706.5849 | 83% | 99%
Business and Law | 2040 | 2225965 | 30673.0181 | 2783.4093 | 13.7796 | 799.7261 | 88% | 99%
Business and Law | 2045 | 2225965 | 30673.0181 | 2783.4093 | 13.7796 | 799.7261 | 88% | 99%
Engineering, Physics and Chemistry | 2025 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Engineering, Physics and Chemistry | 2030 | 1956200 | 35953.3049 | 4375.256 | 18.3792 | 447.1053 | 95% | 100%
Engineering, Physics and Chemistry | 2035 | 3505632 | 70144.3722 | 8738.753 | 20.0091 | 401.1593 | 96% | 100%
Engineering, Physics and Chemistry | 2040 | 4505377 | 90561.7886 | 11192.017 | 20.1008 | 402.5527 | 93% | 100%
Engineering, Physics and Chemistry | 2045 | 5941627 | 115711.7956 | 14077.0783 | 19.4748 | 422.0781 | 93% | 100%
Lower Sproul offices | 2025 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Lower Sproul offices | 2030 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Lower Sproul offices | 2035 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 100% | 100%
Lower Sproul offices | 2040 | 1985373 | 45169.3323 | 4235.373 | 22.7511 | 468.7599 | 90% | 100%
Lower Sproul offices | 2045 | 2792734 | 58444.8103 | 4864.0027 | 20.9275 | 574.1637 | 92% | 99%
Distributed Cooling
Redundancy | Quantity |  | Capacity (tons)
|  | Redundancy | Total | Average | Redundancy
Packaged VAV, DX | 51 | 20% | 3849.9342 | 75.4889 | 100
Water-cooled chiller | 21 | 50% | 10255.694 | 488.3664 | 740
Node | Packaged VAV, DX |  |  |  | Water-cooled chiller
| Quantity | Capacity (tons) | Average | Redundancy | Quantity | Capacity (tons) | Average | Redundancy
Biosciences | 8 | 694.2174 | 86.7772 | 110 | 3 | 1617.137 | 539.0457 | 810
Business and Law | 14 | 942.6365 | 67.3312 | 90 | 5 | 1083.888 | 216.7776 | 330
Engineering, Physics and Chemistry | 22 | 1873.9743 | 85.1806 | 110 | 8 | 2923.104 | 365.388 | 550
Lower Sproul offices | 4 | 281.569 | 70.3923 | 90 | 5 | 4631.565 | 926.313 | 1390
Campus | 48 | 3792.3972 | 79.0083 | 100 | 21 | 10255.694 | 488.3664 | 740
Note on H12: Erica Levine: From DEF
Note on J12: Erica Levine: From DEF
Note on B17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Libraries node was combined with engineering
Note on B28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Libraries node was combined with engineering
Note on I66: Erica Levine: From DEF
Note on K66: Erica Levine: From DEF